## 앞표지
New Leader !! Optimized Preventive Maintenance Solution!!
Digital Motor Protection Relay.
www.samwhadsp.com

## 인트로
New Leader !! SamWha DSP !!
Motor Protection Relay
Digital Motor Protection Relay,SAMWHA DSP VIP-Series , is useful for low voltage motor protection It is aimed to protect a motor against a trouble which is happened from over/under load[current],locked rotor,stall[shock],voltage(power type)/current unbalance,phase loss,reverse phase, short circuit,ground fault,over/under voltage(power type) in motor operation. Also it is able to raise the efficiency for motor operation as being possible to realize a supervision, a protection and a control,furthermore this can be called next generation motor protection relay as making an applicable flexibility for designing and manufacturing the panel in terms of various model with logic input

## ZCT
DSP-ZCT
Zero Phase Current Transformer
○ Technical Specification
Inner diameter(mm) |  | 30 | 50 | 65 | 80 | 100 | 120 | 150 | 200
Z.P. Primary Current |  | 200mA
Z.P. Secondary Current |  | 1.5mA
Operating temperature |  | -25OC ~ +70OC
Storage temperature |  | -35OC ~ +80OC
High potential test |  | AC2KV, 1min
Insulation resistance |  | DC500V, 10MOhm
Operating Frequency |  | 50/60Hz
Error tolerance |  | +,- 10%
Installation |  | Panel Type
Weight(g) |  | 170 | 215 | 275 | 345 | 590 | 785 | 1140 | 1500
○ Dimension
○ Order form
Item | Inner diameter(mm) |  | Reference Code
DSP-ZCT | 30 |  | DSP-ZCT-030
| 50 |  | DSP-ZCT-050
| 65 |  | DSP-ZCT-065
| 80 |  | DSP-ZCT-080
| 100 |  | DSP-ZCT-100
| 120 |  | DSP-ZCT-120
| 150 |  | DSP-ZCT-150
| 200 |  | DSP-ZCT-200
30 ~ 80
100 ~ 200

## 3ct
DSP-3CT
External 3CT of One Body
|  | 3 CT |  |  | Example assembled with DSP-5,C series
○ Technical Specification
| Division |  | Description |  |  |  | Remark
| DSP-3CT |  | CT ratio | 100:5 |  |  | internal shape :octagonal
150:5
200:5
300:5
400:5
| Class |  |  | 1.0, 3.0
| Burden |  |  | 1VA,3VA
| Maximum system Voltage |  |  | 1150V
| Dielectric Voltage |  |  | 4KV/1min
| Usage Frequency |  |  | 50/60Hz
| Thermal withstand current |  |  | 16KA/1sec
| Maximum allowable cable length |  |  | 2.5SQ/10M
| Installation |  |  | Panel Mounting
※ Burden is based on metering class and the accuracy is lower than 1.5% under 1VA
※Do not use this CT except DSP
○ Dimension
○ Order Form
| Item |  | CT Ratio |  |  | Reference
| DSP-3CT |  | 100:5 |  |  | DSP-3CT-100
|  |  | 150:5 |  |  | DSP-3CT-150
|  |  | 200:5 |  |  | DSP-3CT-200
|  |  | 300:5 |  |  | DSP-3CT-300
|  |  | 400:5 |  |  | DSP-3CT-400

## VPFR
○ Feature
· Compact Size , MCU baesd
· Protection :Reverse Phase , Phase Loss
· LED indication for each protection trip
· Trip output : 2-1a(sp-st)
· Auto reset
· Phase loss protection :Available during Forward & Reverse
○ Usage
· Reverse phase protection based on incomming voltage
· Hoist, Crane, Movable Fan
○ Function
· FWD-COM or REV-COM is energized accoding to initial detected state: the protection job is done normally
*Normal direction state :FWD-COM is closed & LED(Green) is turned on
*Reverse direction state:REV-COM is closed & LED(Red) is turned on
· Phase loss in initial state or in working state :such state is shown by LED:L1-R, L2-G, L3-Y /the protection job is stopped
Division |  |  |  |  | Description
Rated Voltage |  | DSP-VPFR22 |  |  | AC160V~300V
|  | DSP-VPFR44 |  |  | AC300V~ 480V
|  | DSP-VPFR69 |  |  | AC590V~ 770V
Indication |  | Normal |  |  | LED(G) Turned ON(Terminal :COM-FOR )
|  | Reverse phase |  |  | LED(R) Turned ON(terminal : COM-REV)
|  | Phase loss - R |  |  | LED - Red , Flickering
|  | Phase loss - S |  |  | LED - Green , Flickering
|  | Phase loss - T |  |  | LED - Yellow , Flickering
Trip Time |  | Reverse phase |  |  | 0.1 (sec)
|  | Phase loss |  |  | 1 (sec)
Frequency |  |  |  |  | 50 / 60 Hz
Trip Output |  | Operation state (FWD-COM, COM-REV) |  | Rating | 1a(1-SPST) * 2 , AC250V/5A,resistive
|  |  |  | Initial | *COM-FOR or COM-REV is closed according to initial direction state:LED indicates a detected state *The protection job is done normally
|  |  |  | Trip | *In case phase loss is detected, the such operated trip relay is trip *All protection job is stopped
Insulation | Insulation Resistance |  | Case-Circuit |  | DC500V Megger,100㏁
| High Voltage Insulation Test |  | Case-Circuit |  | 2.0KV ,50/60Hz, 1min
|  |  | Circuit-Circuit |  | 1.0KV ,50/50Hz, 1min
Environment |  | Temperature | Storage |  | - 30℃ ~ 80℃
|  |  | Operation |  | - 20℃ ~ 65℃
|  | Humidity |  |  | 30 ~ 80% RH, Non-condensing
Consuming Power |  |  |  |  | 0.5 W/max
Installation |  |  |  |  | 35mm DIN-Rail / Panel
○ Dimension
○ Application Sequence Diagram
○ Order Form
| Item |  | Reference |  |  | Possible applied voltage range
| VPFR (Voltage phase relay) |  | DSP-VPFR-22 |  |  | 160 ~ 300VAC
|  |  | DSP-VPFR-44 |  |  | 300 ~ 480VAC
|  |  | DSP-VPFR-69 |  |  | 590 ~ 770VAC

## SS
Motor Protection Relay/Economic Class
DSP-SS/Solid State Type
○ Abstraction
· Compact size/Energy save type
· Current range : 0.5~6A, 3~30A, 5~60A
· Wide protection current range:0.5~600A/3 type and External CT
· Free voltage control power
· Operating indication & checking actual working current : LED/turned on red
· Stable operation in working environment
· Reset:Manual(instant)/Power-off
· Standard type:de-energized in case control power is on(optional type :energized)
○ Usage
· over current protection relay for low voltage induction motor
· Mechanical shock detection
· Current relay job to check a fault
· Possible to replace existing protection relay
○ Function
· Over current : trip after preset o-time
· Phase loss : trp after preset O-Time through preset d-time by over current
· Locked rotor : trip after preset d-time
· To check actual current : LED
· Green LED : control power, operation
· Red LED : trip, over current state
○ How to preset
Division |  | Preset | Description
Starting trip delay time |  | D-TIME | *Preset D-TIME greater than neccessary time to meet safe motor starting due to starting current as turning knob
*Adjustable d-time : 0~60 sec
Over current Trip delay time |  | O-TIME | *Preset neccessary o-time to stop a motor in case of over current condition as turning knob
*Adjustable o-time : 0.2~12 sec
1.Start a motor after positioning current knob to maximum value
2.Slowly turn a knob anti-clockwisely in operating state,then positioned value of knob that red LED flickers is a ponit of actual load current(100%).
3.Nextly turn knob clockwisely a bit of angle right untill red LED is turned off and fix its position
4.Finally this position is matched with 110~120% of actual load current
○ Self-diagnostics
· Keep physically pressing state for TEST button untill preset added time (o-time + d-time) has elapsedwhile the control power is on and motor is stopped, then LED to indicate over current state(OL) will be turned on and trip output is energized as if it trips under motor working state due to over current
· Press Reset button to make reset after test trip,then LED is turned off and return to initial state
○ Technical specification
DIV |  |  |  | Description
Load Current range |  | 06 Type |  | 0.5A∼6A or with external CT
|  | 30 Type |  | 3A∼30A
|  | 60 Type |  | 5A∼60A
Time preset |  | Starting delay time(dt) |  | 0.2∼60sec/def.
|  | over current trip delay time(ot) |  | *0.2∼12sec/def.
Reset |  |  |  | *Manual(instant):reset sw
*Power off:remote
Allowable error |  | Time |  | ±15%
|  | Current |  | ±15%
Control power |  | 24 |  | *24VAC/DC
|  | 220 |  | *90V ∼ 260VAC,50/60Hz
|  | 440 |  | *380V ∼440VAC,50/60Hz
Trip output relay |  | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment |  | temperature | Operation | -25OC∼+70OC
|  |  | Storage | -40OC∼+80OC
|  | Humidity |  | 30∼85%,non-condensing
Insulation Resistence |  |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  |  | *circuit-case:AC 2000V,60Hz, 1 min
*contact-contact:AC1000V,60Hz,1min
Installation |  |  |  | 35mm DIN rail, screw
Power consumption |  |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
DSP-1(Type)-2(Rating current)-3(Control Power)-4(Output initial state)-5(Control power)-6(Auto Reset : optional condition if necessary)
Item | Reference Code |  |  | Remarks
DSP-SS | DSP-SS-06-24-R |  |  | 0.5~6A,24VAC/DC,de-energized initial output
| DSP-SS-06-220-R |  |  | 0.5~6A,90-260VAC,de-energized initial output
| DSP-SS-06-440-R |  |  | 0.5~6A,380-440VAC,de-energized initial output
| DSP-SS-06-24-N |  |  | 0.5~6A,24VAC/DC,energized initial output
| DSP-SS-06-220-N |  |  | 0.5~6A,90-260VAC,energized initial output
| DSP-SS-06-440-N |  |  | 0.5~6A,380-440VAC,energized initial output
| DSP-SS-30-24-R |  |  | 3~30A,24VAC/DC,de-energized initial output
| DSP-SS-30-220-R |  |  | 3~30A,90-260VAC,de-energized initial output
| DSP-SS-30-440-R |  |  | 3~30A,380-440VAC,de-energized initial output
| DSP-SS-30-24-N |  |  | 3~30A,24VAC/DC,energized initial output
| DSP-SS-30-220-N |  |  | 3~30A,90-260VAC,energized initial output
| DSP-SS-30-440-N |  |  | 3~30A,380-440VAC,energized initial output
| DSP-SS-60-24-R |  |  | 5~60A,24VAC/DC,de-energized initial output
| DSP-SS-60-220-R |  |  | 5~60A,90-260VAC,de-energized initial output
| DSP-SS-60-420-R |  |  | 5~60A,380-440VAC,de-energized initial output
| DSP-SS-60-24-N |  |  | 5~60A,24VAC/DC,energized initial output
| DSP-SS-60-220-N |  |  | 5~60A,90-260VAC,energized initial output
| DSP-SS-60-440-N |  |  | 5~60A,380-440VAC,energized initial output

## 3ESSG
Motor Protection Relay/Economic Class
DSP-SS/Solid State Type
○ Abstraction
· Compact size/Energy save type
· Current range : 0.5~6A, 3~30A, 5~60A
→ Over current,Phase loss, Locked rotor, Ground fault : phase loss, loked rotor by over current : ground fault by ZCT
· Wide protection current range:0.5~600A/3 kind of type and External CT
· Free voltage control power
· Operating indication & checking actual working current : LED/turned on red
· Stable operation in working environment
· Reset:Manual(instant)/Power-off
· Standard type:de-energized in case control power is on(optional type :energized)
○ Usage
· over current protection relay for low voltage induction motor
· Mechanical shock detection
· Current relay job to check a fault
· Possible to replace existing protection relay
○ Function
· Over current : trip after preset o-time
· Phase loss : trp after preset O-Time through preset d-time by over current
· Locked rotor : trip after preset d-time
· Ground fault protection by zero phase current : external ZCT
· To check actual current : LED
· Green LED : control power, operation
· Red LED : trip, over current state
· Yellow LED :ground fault
○ How to preset
Division |  | Preset | Description
Starting trip delay time |  | D-TIME | *Preset D-TIME greater than neccessary time to meet safe motor starting due to starting current as turning knob
*Adjustable d-time : 0~60 sec
Over current Trip delay time |  | O-TIME | *Preset neccessary o-time to stop a motor in case of over current condition as turning knob
*Adjustable o-time : 0.2~12 sec
1.Start a motor after positioning current knob to maximum value
2.Slowly turn a knob anti-clockwisely in operating state,then positioned value of knob that red LED flickers is a ponit of actual load current(100%).
3.Nextly turn knob clockwisely a bit of angle right untill red LED is turned off and fix its position
4.Finally this position is matched with 110~120% of actual load current
○ Self-diagnostics
· Keep physically pressing state for TEST button untill preset added time (o-time + d-time) has elapsedwhile the control power is on and motor is stopped, then LED to indicate over current state(OL) will be turned on and trip output is energized as if it trips under motor working state due to over current
· Press Reset button to make reset after test trip,then LED is turned off and return to initial state
○ Technical specification
DIV |  |  |  | Description
Load Current range |  | 06 Type |  | 0.5A∼6A or with external CT
|  | 30 Type |  | 3A∼30A
|  | 60 Type |  | 5A∼60A
Time preset |  | Starting delay time(dt) |  | 0.2∼60sec/def.
|  | over current trip delay time(ot) |  | *0.2∼12sec/def.
Reset |  |  |  | *Manual(instant):reset sw
*Power off:remote
Allowable error |  | Time |  | ±15%
|  | Current |  | ±15%
Control power |  | 24 |  | *24VAC/DC
|  | 220 |  | *90V ∼ 260VAC,50/60Hz
|  | 440 |  | *380V ∼260VAC,50/60Hz
Trip output relay |  | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment |  | temperature | Operation | -25OC∼+70OC
|  |  | Storage | -40OC∼+80OC
|  | Humidity |  | 30∼85%,non-condensing
Insulation Resistence |  |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  |  | *circuit-case:AC 2000V,60Hz, 1 min
*contact-contact:AC1000V,60Hz,1min
Installation |  |  |  | 35mm DIN rail, screw
Power consumption |  |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
DSP-1(Type)-2(Rating current)-3(Control Power)-4(Output initial state)-5(Control power)-6(Auto Reset : optional condition if necessary)
Item | Reference Code |  |  | Remarks
DSP-3ESSG | DSP-3ESSG-06-24-R |  |  | 0.5~6A,24VAC/DC,de-energized initial output
| DSP-3ESSG-06-220-R |  |  | 0.5~6A,90~260VAC,de-energized initial output
| DSP-3ESSG-06-440-R |  |  | 0.5~6A,380~440VAC,de-energized initial output
| DSP-3ESSG-06-24-N |  |  | 0.5~6A,24VAC/DC,energized initial output
| DSP-3ESSG-06-220-N |  |  | 0.5~6A,90~260VAC,energized initial output
| DSP-3ESSG06-440-N |  |  | 0.5~6A,380~440VAC,energized initial output
| DSP-3ESSG-30-24-R |  |  | 3~30A,24VAC/DC,de-energized initial output
| DSP-3ESSG-30-220-R |  |  | 3~30A,90~260VAC,de-energized initial output
| DSP-3ESSG-30-420-R |  |  | 3~30A,380~440VAC,de-energized initial output
| DSP-3ESSG-30-24-N |  |  | 3~30A,24VAC/DC,energized initial output
| DSP-3ESSG-30-220-N |  |  | 3~30A,90~260VAC,energized initial output
| DSP-3ESSG-30-440-N |  |  | 3~30A,380~440VAC,energized initial output
| DSP-3ESSG-60-24-R |  |  | 5~60A,24VAC/DC,de-energized initial output
| DSP-3ESSG-60-220-R |  |  | 5~60A,90~260VAC,de-energized initial output
| DSP-3ESSG-60-420-R |  |  | 5~60A,380~440VAC,de-energized initial output
| DSP-3ESSG-60-24-N |  |  | 5~60A,24VAC/DC,energized initial output
| DSP-3ESSG-60-220-N |  |  | 5~60A,90~260VAC,energized initial output
| DSP-3ESSG-60-440-N |  |  | 5~60A,380~440VAC,energized initial output

## SP
Motor Protection Relay/Economic Class
DSP-SP:direct connection pin type
○ Abstraction
· Direct connection pin type to contactor
· Compact size/Energy save type
· Current range : 0.5~6A, 1~10A, 3~30A
· Unified timer : trip delay and starting delay
· Free voltage control power
· Operating indication & checking actual working current : LED/turned on red
· Stable operation in working environment
· Reset:Manual(instant)/Power-off
· Standard type:de-energized in case control power is on(optional type:energized)
○ Usage
· Over current protection relay for low voltage induction motor
· Mechanical shock detection
· Current relay job to check a fault
· Possible to replace existing protection relay
○ Function
· Over current : trip after preset o-time
· Phase loss : trp after preset o-time by over current
· Locked rotor : trip after preset o-time by over current
· To check actual current : LED
· Green LED : control power, operation
· Red LED : trip, over current state
○ How to preset
Division | Preset | Description
Over current Trip delay time | O-TIME | *Preset neccessary o-time to stop a motor in case of over current condition as turning knob *User should consider both factor of trip delay time and starting delay time for preset o-time *Adjustable o-time : 0.2~30 sec
1.Start a motor after positioning current knob to maximum value position 2.Slowly turn a knob anti-clockwisely in operating state,then positioned value of knob that red LED flickers is a ponit of actual load current(100%). 3.Nextly turn knob clockwisely a bit of angle right untill red LED is turned off and fix its position 4.Finally this position is matched with 110~120% of actual load current
○ Self-diagnostics
· Keep physically pressing state for TEST button untill preset o-time has elapsed while the control power is on and motor is stopped, then LED to indicate over current state(OL) will be turned on and trip output is energized as if it trips under motor working state due to over current
· Press Reset button to make reset after test trip,then LED is turned off and return to initial state
○ Technical specification
DIV |  |  | Description
Load Current range | 06 Type |  | 0.5A∼6A or external CT
| 10 Type |  | 1A∼10A
| 30 Type |  | 3A∼30A
Time preset | over current trip delay time(ot) |  | *0.2∼30sec/def.
Reset |  |  | *Manual(instant):reset sw *Power off:remote
Allowable error | Time |  | ±15%
| Current |  | ±15%
Control power | 24 |  | *24VAC/DC
| 220 |  | *90V ∼ 260VAC,50/60Hz
| 440 |  | *380V ∼260VAC,50/60Hz
Trip output relay | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment | temperature | Operation | -25OC∼+70OC
|  | Storage | -40OC∼+80OC
| Humidity |  | 30∼85%,non-condensing
Insulation Resistance |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  | *circuit-case:AC 2000V,60Hz, 1 min *contact-contact:AC1000V,60Hz,1min
Installation |  |  | 35mm DIN rail, screw
Power consumption |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
DSP-1(Type)-2(Rating current)-3(Control Power)-4(Output initial state)-5(Control power) -6(Auto Reset : optional condition if necessary)
Item | Reference Code |  | Remarks
DSP-SP | DSP-SP-06-24-R |  | 0.5~6A,24VAC/DC,de-energized initial output
| DSP-SP-06-220-R |  | 0.5~6A,90~260VAC,de-energized initial output
| DSP-SP-06-440-R |  | 0.5~6A,380~440VAC,de-energized initial output
| DSP-SP-06-24-N |  | 0.5~6A,24VAC/DC,energized initial output
| DSP-SP-06-220-N |  | 0.5~6A,90~260VAC,energized initial output
| DSP-SP-06-440-N |  | 0.5~6A,380~440VAC,energized initial output
| DSP-SP-10-24-R |  | 1~10A,24VAC/DC,de-energized initial output
| DSP-SP-10-220-R |  | 1~10A,90~260VAC,de-energized initial output
| DSP-SP-10-440-R |  | 1~10A,380~440VAC,de-energized initial output
| DSP-SP-10-24-N |  | 1~10A,24VAC/DC,energized initial output
| DSP-SP-10-220-N |  | 1~10A,90~260VAC,energized initial output
| DSP-SP-10-440-N |  | 1~10A,380~440VAC,energized initial output
| DSP-SP-30-24-R |  | 1~10A,Vde-energized initial output
| DSP-SP-30-220-R |  | 3~30A,90~260VAC,de-energized initial output
| DSP-SP-30-440-R |  | 3~30A,380~440VAC,de-energized initial output
| DSP-SP-30-24-N |  | 3~30A,24VAC/DC,energized initial output
| DSP-SP-30-220-N |  | 3~30A,90~260VAC,energized initial output
| DSP-SP-30-440-N |  | 3~30A,380~440VAC,energized initial output

## ES2
Motor Protection Relay/Economic Class
DSP-ES2:economic solid state & wire through type
○ Abstraction
· Compact size/Energy save type
· Current range : 0.5~6A, 3~30A, 5~60A
· Unified timer : trip delay and starting delay
· Free voltage control power
· Operating indication & checking actual working current : LED/turned on red
· Stable operation in working environment
· Reset:Manual(instant)/Power-off
· Standard type:de-energized in case control power is on(optional type:energized)
○ Usage
· Over current protection relay for low voltage induction motor
· Mechanical shock detection
· Current relay job to check a fault
· Possible to replace existing protection relay
○ Function
· Over current : trip after preset o-time
· Phase loss : trp after preset o-time by over current
· Locked rotor : trip after preset o-time by over current
· To check actual current : LED
· Green LED : control power, operation
· Red LED : trip, over current state
○ How to preset
Division | Preset | Description
Over current Trip delay time | O-TIME | *Preset neccessary o-time to stop a motor in case of over current condition as turning knob *User should consider both factor of trip delay time and starting delay time for preset o-time *Adjustable o-time : 0.2~30 sec
1.Start a motor after positioning current knob to maximum value position 2.Slowly turn a knob anti-clockwisely in operating state,then positioned value of knob that red LED flickers is a point of actual load current(100%). 3.Nextly turn knob clockwisely a bit of angle right untill red LED is turned off and fix its position 4.Finally this position is matched with 110~120% of actual load current
○ Self-diagnostics
· Keep physically pressing state for TEST button untill preset o-time has elapsed while the control power is on and motor is stopped, then LED to indicate over current state(OL) will be turned on and trip output is energized as if it trips under motor working state due to over current
· Press Reset button to make reset after test trip,then LED is turned off and return to initial state
○ Technical specification
3IV |  |  | Description
Load Current range | 06 Type |  | 0.5A∼6A or external CT
| 30 Type |  | 3A∼30A
| 60 Type |  | 5A∼60A
Time preset | over current trip delay time(ot) |  | *0.2∼30sec/def.
Reset |  |  | *Manual(instant):reset sw *Power off:remote
Allowable error | Time |  | ±15%
| Current |  | ±15%
Control power | 24 |  | *24VAC/DC
| 220 |  | *90V ∼ 260VAC,50/60Hz
| 440 |  | *380V ∼260VAC,50/60Hz
Trip output relay | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment | temperature | Operation | -25OC∼+70OC
|  | Storage | -40OC∼+80OC
| Humidity |  | 30∼85%,non-condensing
Insulation Resistance |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  | *circuit-case:AC 2000V,60Hz, 1 min *contact-contact:AC1000V,60Hz,1min
Installation |  |  | 35mm DIN rail, screw
Power consumption |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
DSP-1(Type)-2(Rating current)-3(Control Power)-4(Output initial state)-5(Control power)
Item | Reference Code |  | Remarks
DSP-ES2 | DSP-ES2-06-24-R |  | 0.5~6A,24VAC/DC,de-energized initial output
| DSP-ES2-06-220-R |  | 0.5~6A,90~260VAC,de-energized initial output
| DSP-ES2-06-420-R |  | 0.5~6A,380~440VAC,de-energized initial output
| DSP-ES2-06-24-N |  | 0.5~6A,24VAC/DC,energized initial output
| DSP-ES2-06-220-N |  | 0.5~6A,90~260VAC,energized initial output
| DSP-ES2-06-440-N |  | 0.5~6A,380~440VAC,energized initial output
| DSP-ES2-30-24-R |  | 3~30A,24VAC/DC,de-energized initial output
| DSP-ES2-30-220-R |  | 3~30A,90~260VAC,de-energized initial output
| DSP-ES2-30-420-R |  | 3~30A,380~440VAC,de-energized initial output
| DSP-ES2-30-24-N |  | 3~30A,24VAC/DC,energized initial output
| DSP-ES2-30-220-N |  | 3~30A,90~260VAC,energized initial output
| DSP-ES2-30-440-N |  | 3~30A,380~440VAC,,energized initial output
| DSP-ES2-60-24-R |  | 5~60A,24VAC/DC,de-energized initial output
| DSP-ES2-60-220-R |  | 5~60A,90~260VAC,de-energized initial output
| DSP-ES2-60-420-R |  | 5~60A,380~440VAC,de-energized initial output
| DSP-ES2-60-24-N |  | 5~60A,24VAC/DC,energized initial output
| DSP-ES2-60-220-N |  | 5~60A,90~260VAC,energized initial output
| DSP-ES2-60-440-N |  | 5~60A,380~440VAC,energized initial output

## UCR
Under Current Protection Relay
DSP-UCR
○ Abstraction
· Compact size/Energy save type
· Current range : 0.5~6A, 3~30A, 5~60A
· Unified timer : trip delay and starting delay
· Free voltage control power
· Operating indication & checking actual working current : LED/turned on red
· Stable operation in working environment
· Reset:Manual(instant)/Power-off
· Standard type:de-energized in case control power is on(optional type:energized)
○ Usage
· To prevent motor dry running
· To make alarm for a disconnection of input line to heater
· Current relay job to check a fault
· Possible to replace existing protection relay
○ Function
· Under current : trip after preset o-time
· To check actual current : LED
· Green LED : control power, operation
· Red LED : trip, under current state
○ How to preset
Division | Preset | Description
Over current Trip delay time | O-TIME | *Preset neccessary o-time to stop a motor in case of over current condition as turning knob *User should consider both factor of trip delay time and starting delay time for preset o-time *Adjustable o-time : 0.2~30 sec
1.Start a motor after positioning current knob to minimum value position 2.Slowly turn a knob clockwisely in operating state,then positioned value of knob that red LED flickers is a point of actual load current(100%). 3.Nextly turn knob anti-clockwisely a bit of angle right untill red LED is turned off and fix its position 4.Finally this position is matched with 80~90% of actual load current
○ Self-diagnostics
· Keep physically pressing state for TEST button untill preset o-time has elapsed while the control power is on and motor is stopped, then LED to indicate over current state(OL) will be turned on and trip output is energized as if it trips under motor working state due to under current
· Press Reset button to make reset after test trip,then LED is turned off and return to initial state
○ Technical specification
3IV |  |  | Description
Load Current range | 06 Type |  | 0.5A∼6A or external CT
| 30 Type |  | 3A∼30A
| 50 Type |  | 5A∼50A
Time preset | over current trip delay time(ot) |  | *0.2∼30sec/def.
Reset |  |  | *Manual(instant):reset sw *Power off:remote
Allowable error | Time |  | ±15%
| Current |  | ±15%
Control power | 24 |  | *24VAC/DC
| 220 |  | *90V ∼ 260VAC,50/60Hz
| 440 |  | *380V ∼260VAC,50/60Hz
Trip output relay | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment | temperature | Operation | -25OC∼+70OC
|  | Storage | -40OC∼+80OC
| Humidity |  | 30∼85%,non-condensing
Insulation Resistance |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  | *circuit-case:AC 2000V,60Hz, 1 min *contact-contact:AC1000V,60Hz,1min
Installation |  |  | 35mm DIN rail, screw
Power consumption |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
DSP-1(Type)-2(Rating current)-3(Control Power)-4(Output initial state)-5(Control power)
Item | Reference Code |  | Remarks
DSP-UCR | DSP-UCR-06-24-R |  | 0.5~6A,24VAC/DC,de-energized initial output
| DSP-UCR-06-220-R |  | 0.5~6A,90~260VAC,de-energized initial output
| DSP-UCR-06-440-R |  | 0.5~6A,380~440VAC,de-energized initial output
| DSP-UCR-06-24-N |  | 0.5~6A,24VAC/DC,energized initial output
| DSP-UCR-06-220-N |  | 0.5~6A,90~260VAC,energized initial output
| DSP-UCR-06-440-N |  | 0.5~6A,380~440VAC,energized initial output
| DSP-UCR-30-24-R |  | 1~10A,24VAC/DC,de-energized initial output
| DSP-UCR-30-220-R |  | 3~30A,90~260VAC,de-energized initial output
| DSP-UCR-30-440-R |  | 3~30A,380~440VAC,de-energized initial output
| DSP-UCR-30-24-N |  | 3~30A,24VAC/DC,energized initial output
| DSP-UCR-30-220-N |  | 3~30A,90~260VAC,energized initial output
| DSP-UCR-30-440-N |  | 3~30A,380~440VAC,energized initial output
| DSP-UCR-50-24-R |  | 5~50A,24VAC/DC,de-energized initial output
| DSP-UCR-50-220-R |  | 5~50A,90~260VAC,de-energized initial output
| DSP-UCR-50-440-R |  | 5~50A,380~440VAC,de-energized initial output
| DSP-UCR-50-24-N |  | 5~50A,24VAC/DC,energized initial output
| DSP-UCR-50-220-N |  | 5~50A,90~260VAC,,energized initial output
| DSP-UCR-50-440-N |  | 5~50A,,380~440VAC,energized initial output

## ES
Motor Protection Relay/Economic Class
DSP-ES:economic solid state & wire through type
○ Abstraction
· Compact size/Energy save type
· Current range : 0.5~6A, 3~30A, 5~60A
· Unified timer : trip delay and starting delay
· Free voltage control power
· Operating indication & checking actual working current : LED/turned on red
· Stable operation in working environment
· Reset:Manual(instant)/Power-off
· Standard type:de-energized in case control power is on(optional type:energized)
○ Usage
· Over current protection relay for low voltage induction motor
· Mechanical shock detection
· Current relay job to check a fault
· Possible to replace existing protection relay
○ Function
· Over current : trip after preset o-time
· Phase loss : trp after preset o-time by over current
· Locked rotor : trip after preset o-time by over current
· To check actual current : LED
· Green LED : control power, operation
· Red LED : trip, over current state
○ How to preset
Division | Preset | Description
Over current Trip delay time | O-TIME | *Preset neccessary o-time to stop a motor in case of over current condition as turning knob *User should consider both factor of trip delay time and starting delay time for preset o-time *Adjustable o-time : 0.2~30 sec
1.Start a motor after positioning current knob to maximum value position 2.Slowly turn a knob anti-clockwisely in operating state,then positioned value of knob that red LED flickers is a point of actual load current(100%). 3.Nextly turn knob clockwisely a bit of angle right untill red LED is turned off and fix its position 4.Finally this position is matched with 110~120% of actual load current
○ Self-diagnostics
· Keep physically pressing state for TEST button untill preset o-time has elapsed while the control power is on and motor is stopped, then LED to indicate over current state(OL) will be turned on and trip output is energized as if it trips under motor working state due to over current
· Press Reset button to make reset after test trip,then LED is turned off and return to initial state
○ Technical specification
3IV |  |  | Description
Load Current range | 06 Type |  | 0.5A∼6A or external CT
| 30 Type |  | 3A∼30A
| 60 Type |  | 5A∼60A
Time preset | over current trip delay time(ot) |  | *0.2∼30sec/def.
Reset |  |  | *Manual(instant):reset sw *Power off:remote
Allowable error | Time |  | ±15%
| Current |  | ±15%
Control power | 24 |  | *24VAC/DC
| 220 |  | *90V ∼ 260VAC,50/60Hz
| 440 |  | *380V ∼260VAC,50/60Hz
Trip output relay | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment | temperature | Operation | -25OC∼+70OC
|  | Storage | -40OC∼+80OC
| Humidity |  | 30∼85%,non-condensing
Insulation Resistance |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  | *circuit-case:AC 2000V,60Hz, 1 min *contact-contact:AC1000V,60Hz,1min
Installation |  |  | 35mm DIN rail, screw
Power consumption |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
DSP-1(Type)-2(Rating current)-3(Control Power)-4(Output initial state)-5(Control power)
Item | Reference Code |  | Remarks
DSP-ES | DSP-ES-06-24-R |  | 0.5~6A,24VAC/DC,de-energized initial output
| DSP-ES-06-220-R |  | 0.5~6A,90~260VAC,de-energized initial output
| DSP-ES-06-420-R |  | 0.5~6A,380~440VAC,de-energized initial output
| DSP-ES-06-24-N |  | 0.5~6A,24VAC/DC,energized initial output
| DSP-ES-06-220-N |  | 0.5~6A,90~260VAC,energized initial output
| DSP-ES-06-440-N |  | 0.5~6A,380~440VAC,energized initial output
| DSP-ES-30-24-R |  | 3~30A,24VAC/DC,de-energized initial output
| DSP-ES-30-220-R |  | 3~30A,90~260VAC,de-energized initial output
| DSP-ES-30-420-R |  | 3~30A,380~440VAC,de-energized initial output
| DSP-ES-30-24-N |  | 3~30A,24VAC/DC,energized initial output
| DSP-ES-30-220-N |  | 3~30A,90~260VAC,energized initial output
| DSP-ES-30-440-N |  | 3~30A,380~440VAC,,energized initial output
| DSP-ES-60-24-R |  | 5~60A,24VAC/DC,de-energized initial output
| DSP-ES-60-220-R |  | 5~60A,90~260VAC,de-energized initial output
| DSP-ES-60-420-R |  | 5~60A,380~440VAC,de-energized initial output
| DSP-ES-60-24-N |  | 5~60A,24VAC/DC,energized initial output
| DSP-ES-60-220-N |  | 5~60A,90~260VAC,energized initial output
| DSP-ES-60-440-N |  | 5~60A,380~440VAC,energized initial output

## 3ESS
Motor Protection Relay
DSP-3ESS
○ Abstraction
· Compact size/Energy save type
· Current range : 0.5~6A, 3~30A, 5~60A
· Over current,Phase loss, Locked rotor : phase loss, loked rotor by over current : reverse phase by incoming voltage
· Wide protection current range :0.5~600A/3 kind of type and External CT
· Free voltage control power
· Operating indication & checking actual working current : LED/turned on red
· Stable operation in working environment
· Reset:Manual(instant)/Power-off
· Standard type:de-energized in case control power is on(optional type : energized)
○ Usage
· Reverse phase by incoming voltage:instant trip
· Over current protection relay for low voltage induction motor
· Mechanical shock detection
· Current relay job to check a fault
· Possible to replace existing protection relay
○ Function
· Over current : trip after preset o-time
· Reverse phase by incoming voltage:instant trip
· Phase loss : trp after preset o-time by over current
· Locked rotor : trip after preset d-time
· To check actual current : LED
· Green LED : control power, operation
· Red LED : trip, over current state
· Yellow LED : reverse phase
○ How to preset
Division | Preset | Description
Starting trip delay time | D-TIME | *Preset d-time greater than neccessary time to meet safe motor starting due to starting current as turning knob *Adjustable d-time : 0~60sec
Over current Trip delay time | O-TIME | *Preset neccessary o-time to stop a motor in case of over current condition as turning knob *Adjustable o-time : 0.2~12 sec
1.Start a motor after positioning current knob to maximum value position 2.Slowly turn a knob anti-clockwisely in operating state,then positioned value of knob that red LED flickers is a ponit of actual load current(100%). 3.Nextly turn knob clockwisely a bit of angle right untill red LED is turned off and fix its position 4.Finally this position is matched with 110~120% of actual load current
○ Self-diagnostics
· Keep physically pressing state for TEST button untill preset added time (o-time + d-time) has elapsedwhile the control power is on and motor is stopped, then LED to indicate over current state(OL) will be turned on and trip output is energized as if it trips under motor working state due to over current
· Press Reset button to make reset after test trip,then LED is turned off and return to initial state
○ Technical specification
DIV |  |  | Description
Load Current range | 06 Type |  | 0.5A∼6A or external CT
| 30 Type |  | 3A∼30A
| 60 Type |  | 5A∼60A
Time preset | Starting delay time(dt) |  | *0.2∼60sec/def.
| over current trip delay time(ot) |  | *0.2∼12sec/def.
Reset |  |  | *Manual(instant):reset sw *Power off:remote
Allowable error | Time |  | ±15%
| Current |  | ±15%
Control power | 24 |  | *24VAC/DC
| 220 |  | *90V ∼ 260VAC,50/60Hz
| 440 |  | *380V ∼260VAC,50/60Hz
Trip output relay | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment | temperature | Operation | -25OC∼+70OC
|  | Storage | -40OC∼+80OC
| Humidity |  | 30∼85%,non-condensing
Insulation Resistance |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  | *circuit-case:AC 2000V,60Hz, 1 min *contact-contact:AC1000V,60Hz,1min
Installation |  |  | 35mm DIN rail, screw
Power consumption |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
DSP-1(Type)-2(Rating current)-3(Control Power)-4(Output initial state)-5(Control power)-6(Auto Reset : optional condition if necessary)
Item | Reference Code |  | Remarks
DSP-3ESS | DSP-3ESS-06-24-R |  | 0.5~6A,24VAC/DC,de-energized initial output
| DSP-3ESS-06-220-R |  | 0.5~6A,90~260VAC,de-energized initial output
| DSP-3ESS-06-420-R |  | 0.5~6A,380~440VAC,de-energized initial output
| DSP-3ESS-06-24-N |  | 0.5~6A,24VAC/DC,energized initial output
| DSP-3ESS-06-220-N |  | 0.5~6A,90~260VAC,energized initial output
| DSP-3ESS-06-440-N |  | 0.5~6A,380~440VAC,energized initial output
| DSP-3ESS-30-24-R |  | 3~30A,24VAC/DC,de-energized initial output
| DSP-3ESS-30-220-R |  | 3~30A,90~260VAC,de-energized initial output
| DSP-3ESS-30-420-R |  | 3~30A,380~440VAC,de-energized initial output
| DSP-3ESS-30-24-N |  | 3~30A,24VAC/DC,energized initial output
| DSP-3ESS-30-220-N |  | 3~30A,90~260VAC,energized initial output
| DSP-3ESS-30-440-N |  | 3~30A,380~440VAC,,energized initial output
| DSP-3ESS-60-24-R |  | 5~60A,24VAC/DC,de-energized initial output
| DSP-3ESS-60-220-R |  | 5~60A,90~260VAC,de-energized initial output
| DSP-3ESS-60-420-R |  | 5~60A,380~440VAC,de-energized initial output
| DSP-3ESS-60-24-N |  | 5~60A,24VAC/DC,energized initial output
| DSP-3ESS-60-220-N |  | 5~60A,90~260VAC,energized initial output
| DSP-3ESS-60-440-N |  | 5~60A,380~440VAC,energized initial output
Auto reset type * Reference code : Basic code + AR(suffix code)
Item | Reference Code |  | Remarks
DSP-3ESS | DSP-3ESS-06-24-R-AR |  | 0.5~6A,24VAC/DC,de-energized initial output, auto reset
| DSP-3ESS-06-220-R-AR |  | 0.5~6A,90~260VAC,de-energized initial output, auto reset
| DSP-3ESS-06-440-R-AR |  | 0.5~6A,380~440VAC,de-energized initial output, auto reset
| DSP-3ESS-06-24-N-AR-AR |  | 0.5~6A,24VAC/DC,energized initial output, auto reset
| DSP-3ESS-06-220-N-AR-AR |  | 0.5~6A,90~260VAC,energized initial output, auto reset
| DSP-3ESS-06-440-N-AR |  | 0.5~6A,380~440VAC,energized initial output, auto reset
| DSP-3ESS-30-24-R-AR |  | 3~30A,24VAC/DC,de-energized initial output, auto reset
| DSP-3ESS-30-220-R-AR |  | 3~30A,,90~260VAC,de-energized initial output, auto reset
| DSP-3ESS-30-440-R |  | 3~30A,380~440VAC,de-energized initial output, auto reset
| DSP-3ESS-30-24-N |  | 3~30A,24VAC/DC,nergized initial output, auto reset
| DSP-3ESS-30-220-N |  | 3~30A,90~260VAC,energized initial output, auto reset
| DSP-3ESS-30-440-N |  | 3~30A,380~440VAC,energized initial output, auto reset
| DSP-3ESS-60-24-R |  | 5~60A,24VAC/DC,de-energized initial output, auto reset
| DSP-3ESS-60-220-R |  | 5~60A,90~260VAC,de-energized initial output, auto reset
| DSP-3ESS-60-440-R |  | 5~60A,380~440VAC,de-energized initial output, auto reset
| DSP-3ESS-60-24-N |  | 5~60A,24VAC/DC,energized initial output, auto reset
| DSP-3ESS-60-220-N |  | 5~60A,90~260VAC,energized initial output, auto reset
| DSP-3ESS-60-440-N |  | 5~60A,380~440VAC,energized initial output, auto reset

## 주문코드 (2) (hidden)
주문방법
UMP | P | O | M | I | 06 | T | F
형명 | 용도 | 특성 | 부착방식 | 보호기능 | 정격전류 | 체결방식 | 조작전압
UMP | P : 전력형(고급형) | O : 기본 | M : 분리형 Meter | Z : ZCT(외장형) | 03 : 0.2~5A (외부CT조합형) | T : 관통식 | F : 85~260VAC /120~370VDC
| R : 전류형(절연저항형) | C : 통신 | L : 일체형 Meter | I ZCT(내장형) | 06 : 0.2~6A (외부CT조합형) | S : 단자식
| 5 : 전류형(일반형) | T : 4~20mA |  |  | 10 : 0.5~10A (외부CT조합형) |  | D : 24VDC
| K : 전력형(보급형) | S : 단락 |  |  | 70 : 0.2~70A
C : 전류형(보급형)
¦ 표준품 주문코드[ PM TYPE ] ¦ |  |  |  | ¦ Accessory코드[ PM TYPE ] ¦
TYPE | 기능설명 |  |  | TYPE | 기능설명
UMP-POM | 기본형 + 4 ~ 20mA + 분리형 Meter |  |  | UMPPM | 전력계전기 분리형 Meter
UMP-PCM | 기본형 + 4 ~ 20mA + 통신 + 분리형 Meter |  |  | UMPPL | 전력계전기 일체형 Meter
UMP-POL | 기본형 + 4 ~ 20mA + 일체형 Meter |  |  | UMPCU | 통신Unit
UMP-PCL | 기본형 + 4 ~ 20mA + 통신 + 일체형 Meter |  |  | UMPMCWR | 기록계
¦ 표준품 주문코드[ RM TYPE ] ¦ |  |  |  | ¦ Accessory코드[ RM TYPE ] ¦
TYPE | 기능설명 |  |  | TYPE |  | 기능설명
UMP-ROM | 기본형 + 4 ~ 20mA + 분리형 Meter |  |  | UMPRM |  | 절연저항측정계전기 분리형 Meter
UMP-RCM | 기본형 + 4 ~ 20mA + 통신 + 분리형 Meter |  |  | UMPRL |  | 절연저항측정계전기 일체형 Meter
UMP-ROL | 기본형 + 4 ~ 20mA + 분리형 Meter |  |  | UMPCU |  | 통신 Unit
UMP-RCL | 기본형 + 4 ~ 20mA + 통신 + 분리형 Meter |  |  | UMPMCWR |  | 기록계
¦ 표준품 주문코드[ 5M TYPE ] ¦ |  |  |  | ¦ Accessory코드[ 5M TYPE ] ¦
TYPE | 기능설명 |  |  | TYPE |  | 기능설명
UMP-5OM | 기본형 + 분리형 Meter |  |  | UMP5OM |  | 전류계전기 분리형 Meter(기본)
UMP-5CM | 기본형 + 통신(485) + 분리형 Meter |  |  | UMP5CM |  | 전류계전기 분리형 Meter(통신)
UMP-5TM | 기본형 + 4 ~ 20mA + 분리형 Meter |  |  | UMP5TM |  | 전류계전기 분리형 Meter(4~20mA)
UMP-5OL | 기본형 + 일체형 Meter
UMP-5CL | 기본형 + 통신(485) + 일체형 Meter
UMP-5TL | 기본형 + 4 ~ 20mA + 일체형 Meter
¦ 표준품 주문코드[ CM TYPE ] ¦ |  |  |  | ¦ Accessory코드[ CM TYPE ] ¦
TYPE | 기능설명 |  |  | TYPE |  | 기능설명
UMP-COM | 기본형 + 분리형 Meter |  |  | UMPCOM |  | 전류계전기 분리형 Meter(기본)
UMP-CCM | 기본형 + 통신(485) + 분리형 Meter |  |  | UMPCCM |  | 전류계전기 분리형 Meter(통신)
UMP-CTM | 기본형 + 4 ~ 20mA + 분리형 Meter |  |  | UMPCTM |  | 전류계전기 분리형 Meter(4~20mA)
UMP-COL | 기본형 + 일체형 Meter
UMP-CCL | 기본형 + 통신(485) + 일체형 Meter
UMP-CTL | 기본형 + 4 ~ 20mA + 일체형 Meter
¦ 표준품 주문코드[ KM TYPE ] ¦ |  |  |  | ¦ Accessory코드[ KM TYPE ] ¦
TYPE | 기능설명 |  |  | TYPE |  | 기능설명
UMP-KOM | 기본형 + 분리형 Meter |  |  | UMPKOM |  | 전력계전기 분리형 Meter(기본)
UMP-KCM | 기본형 + 통신(485) + 분리형 Meter |  |  | UMPKCM |  | 전력계전기 분리형 Meter(통신)
UMP-KTM | 기본형 + 4 ~ 20mA + 분리형 Meter |  |  | UMPKTM |  | 전력계전기 분리형 Meter(4~20mA)
UMP-KOL | 기본형 + 일체형 Meter
UMP-KCL | 기본형 + 통신(485) + 일체형 Meter
UMP-KTL | 기본형 + 4 ~ 20mA + 일체형 Meter
Note on K3: a: F:Free Voltage DC:24VDC

## OVR
Over Voltage Protection Relay
DSP-OVR
○ Abstraction
· Compact size/Energy save type
· Over Voltage protection range : :22 type/220~300V :38 type/380~460V
· Free voltage control power
· Operating indication & checking actual working voltage : LED/turned on red
· Stable operation in working environment
· Auto Reset
· Standard type:de-energized in case control power is on(optional type : energized)
○ Usage
· Over voltage protection relay for generator
· Voltage relay job to check a fault
○ Function
· Over voltage : trip after preset o-time
· To check actual voltage : LED
· Green LED : control power, operation
· Red LED : trip, over voltage state
○ How to preset
Division | Preset | Description
Over voltage Trip delay time | O-TIME | *Preset neccessary o-time to protect over voltage as turning knob *Adjustable o-time : 0.2~12 sec
1.Start a generator after positioning voltage adjusting knob to maximum value position 2.Slowly turn a knob anti-clockwisely in operating state,then positioned value of knob that red LED flickers is a ponit of actual voltage(100%). 3.Nextly turn knob clockwisely a bit of angle right untill red LED is turned off and fix its position 4.Finally this position is matched with 110~120% of actual voltage
○ Technical specification
3IV |  |  | Description
Voltage range | 22 Type |  | 220~300VAC
| 38 Type |  | 380~460VAC
Time preset | over voltage trip delay time(ot) |  | *0.2∼12sec/def.
Reset |  |  | *Auto
Allowable error | Time |  | ±15%
| Voltage |  | ±15%
Control power |  |  | *220VAC,50/60Hz
Trip output relay | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment | temperature | Operation | -25OC∼+70OC
|  | Storage | -40OC∼+80OC
| Humidity |  | 30∼85%,non-condensing
Insulation Resistance |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  | *circuit-case:AC 2000V,60Hz, 1 min *contact-contact:AC1000V,60Hz,1min
Installation |  |  | 35mm DIN rail, screw
Power consumption |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
DSP-1(Type)-2(Rating voltage)-3(Output initial state)
Item | Reference Code |  | Remarks
DSP-OVR | DSP-OVR-22-R |  | Over voltage:220~300VAC,de-energized initial output
| DSP-OVR-38-R |  | Over voltage:380~460VAC,de-energized initial output
| DSP-OVR-22-N |  | Over voltage:220~300VAC,energized initial output
| DSP-OVR-38-N |  | Over voltage:380~460VAC,energized initial output

## UVR
Under Voltage Protection Relay
DSP-UVR
○ Abstraction
· Compact size/Energy save type
· Under Voltage protection range : :22 type/160~220V :38 type/300~380V
· Free voltage control power
· Operating indication & checking actual working voltage : LED/turned on red
· Stable operation in working environment
· Auto Reset
· Standard type:de-energized in case control power is on(optional type : energized)
○ Usage
· Over voltage protection relay for generator
· Voltage relay job to check a fault
○ Function
· Over voltage : trip after preset o-time
· To check actual voltage : LED
· Green LED : control power, operation
· Red LED : trip, over voltage state
○ How to preset
Division | Preset | Description
Under voltage Trip delay time | O-TIME | *Preset neccessary o-time to protect under voltage as turning knob *Adjustable o-time : 0.2~12 sec
1.Start a generator after positioning voltage adjusting knob to minimum value position 2.Slowly turn a knob clockwisely in operating state,then positioned value of knob that red LED flickers is a ponit of actual voltage(100%). 3.Nextly turn knob anti-clockwisely a bit of angle right untill red LED is turned off and fix its position 4.Finally this position is matched with 80~90% of actual voltage
○ Technical specification
3IV |  |  | Description
Voltage range | 22 Type |  | 160~220VAC
| 38 Type |  | 300~380VAC
Time preset | Under voltage trip delay time(ot) |  | *0.2∼12sec/def.
Reset |  |  | *Auto
Allowable error | Time |  | ±15%
| Voltage |  | ±15%
Control power |  |  | *220VAC,50/60Hz
Trip output relay | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment | temperature | Operation | -25OC∼+70OC
|  | Storage | -40OC∼+80OC
| Humidity |  | 30∼85%,non-condensing
Insulation Resistance |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  | *circuit-case:AC 2000V,60Hz, 1 min *contact-contact:AC1000V,60Hz,1min
Installation |  |  | 35mm DIN rail, screw
Power consumption |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
DSP-1(Type)-2(Rating voltage)-3(Output initial state)
Item | Reference Code |  | Remarks
DSP-UVR | DSP-UVR-22-R |  | Under voltage:160~220VAC,de-energized initial output
| DSP-UVR-38-R |  | Under voltage:300~380VAC,de-energized initial output
| DSP-UVR-22-N |  | Under voltage:160~220VAC,energized initial output
| DSP-UVR-38-N |  | Under voltage:300~380VAC,energized initial output

## GR
Ground Fault Protection Relay
DSP-GR
○ Abstraction
· Compact size/Energy save type
· Ground fault current range : 50mA~600mA :sensed by ZCT[200mA/1.5mA] :sensed by 100/5 CT(optional type)
· Free voltage control power
· Operating indication & checking actual ground fault current : LED/turned on red
· Stable operation in working environment
· Reset:Auto/Manual(instant)/Power-off
· De-energized trip output in case control power is on
○ Usage
· Ground fault protection for generator, motor
· Ground fault protection for Line
○ Function
· Ground fault protection : trip after preset o-time
· Ground fault protection by zero phase current : external ZCT
· To check actual current : LED
· Red LED : trip, ground fault state
○ How to preset
Division | Preset | Description
Over current Trip delay time | O-TIME | *Preset neccessary o-time to stop a motor in case of over current condition as turning knob *Adjustable o-time : 0.1~3 sec
○ Self-diagnostics
· Keep physically pressing state for TEST button untill preset o-time has elapsed while the control power is on, then LED to indicate ground fault current state(OL) will be turned on and trip output is energized as if it trips due to ground fault current
· Press Reset button to make reset after test trip,then LED is turned off and return to initial state
○ Technical specification
DIV |  |  | Description
Ground fault current range |  |  | 50mA∼600mA
Ground fault current trip delay time(ot) |  |  | *0.1∼3sec/def.
Reset |  |  | *Manual(instant):reset sw *Power off:remote
Allowable error | Time |  | ±15%
| Current |  | ±15%
Control power | 24 |  | *24VAC/DC
| 220 |  | *90V ∼ 260VAC,50/60Hz
| 440 |  | *380V ∼440VAC,50/60Hz
Trip output relay | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment | temperature | Operation | -25OC∼+70OC
|  | Storage | -40OC∼+80OC
| Humidity |  | 30∼85%,non-condensing
Insulation Resistance |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  | *circuit-case:AC 2000V,60Hz, 1 min *contact-contact:AC1000V,60Hz,1min
Installation |  |  | 35mm DIN rail, screw
Power consumption |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
Item | Reference Code |  | Remarks
DSP-GR | DSP-GR-24 |  | Optional,24VAC/DC,de-energized initial output
| DSP-GR-220 |  | 90~260VAC,de-energized initial output
| DSP-GR-440 |  | 380~440VAC,de-energized initial output

## NGR
Non-Ground Detection Relay
DSP-NGR
○ Abstraction
· Compact size/Energy save type
· Non-ground detection for electrical machine
· Only available for three phase system with connection directly to earth
· Free voltage control power
· Operating indication:LED/turned on red
· Stable operation in working environment
· Auto Reset
· De-energized in case control power is on
○ Usage
· To alert non-ground state of electrical device case like motor,transformer,etc.
· Trip output relay is not energized in case of normal ground connection to earth
○ Function
· Alert for non-grounded state :Red LED
· Control power, operation : green LED
· Self-diagnostic : press a test button after the control power is loaded, then trip output relay is energized as red LED is turned on and make reset as pressing reset button
○ Technical specification
DIV |  |  | Description
Incoming line voltage |  |  | * 220~440VAC
Non-ground detection trip delay time |  |  | * within 0.1sec.
Reset |  |  | * Manual(instant):reset sw * Power off:remote
Allowable error | Time |  | ±15%
| Current |  | ±15%
Control power |  |  | * 90~260VAC,50/60Hz
Trip output relay | Main : 95-96-98 |  | 1c(1-SPDT),3A/Resistive
Application environment | temperature | Operation | -25OC∼+70OC
|  | Storage | -40OC∼+80OC
| Humidity |  | 30∼85%,non-condensing
Insulation Resistance |  |  | 50 Mohm or more/500VDC, circuit-case
Withstanding Voltage |  |  | *circuit-case:AC 2000V,60Hz, 1 min *contact-contact:AC1000V,60Hz,1min
Installation |  |  | 35mm DIN rail, screw
Power consumption |  |  | 0.5W Max
○ Dimension
○ Application Sequence Diagram
○ Order form
Item | Reference Code |  | Remarks
DSP-NGR | DSP-NGR |  | control power:160~220VAC,de-energized initial output